NEXP SERIES EXPLOSION-PROOF PREMIUM EFFICIENCY THREE PHASE INDUCTION MOTOR (FRAME143-449)

Technical Agreement

(Draft)

- General

This technical agreement is made between Nanyang and WWE to carry out PO execution. This agreement should be followed strictly unless otherwise specified clearly on PO.

- Ratings

Table 1 the correlation between output and frame size

| HP | 3600 (60Hz) 3000(50Hz) RPM | 1800(60Hz) 1500(50Hz) RPM | 1200 (60Hz) 1000(50Hz) RPM |
| --- | --- | --- | --- |
| 1 |  | 143T | 145T |
| 1.5 | 143T | 145T | 182T |
| 2 | 145T | 145T | 184T |
| 3 | 182T | 182T | 213T |
| 5 | 184T | 184T | 215T |
| 7.5 | 213T | 213T | 254T |
| 10 | 215T | 215T | 256T |
| 15 | 254T | 254T | 284T |
| 20 | 256T | 256T | 286T |
| 25 | 284TS | 284TS/T | 324T |
| 30 | 286TS | 286TS/T | 326T |
| 40 | 324TS | 324TS/T | 364T |
| 50 | 326TS | 326TS/T | 365T |
| 60 | 364TS | 364TS/T | 404T |
| 75 | 365TS | 365TS/T | 405T |
| 100 | 405TS | 405TS/T | 444T |
| 125 | 444TS | 444TS/T | 445T |
| 150 | 445TS | 445TS/T | 447T |
| 200 | 447TS | 447TS/T | 449T |
| 250 | 449TS | 449TS/T |  |

- Standard Features

| Item | NEXP Series |
| --- | --- |
| Power | 1-250HP |
| Poles | 2, 4, 6 |
| Certificate | UL certificate E228654; CSA certificate 1224673; |
| Altitude | 3300ft |
| Ambient temp. | 55℃： service factor 1.15 with temp. rise within class F (115℃) |
| Balancing and Vibration | G1.0 Standard: 0. 060 in/sec (p) |
| Bearing cover | 140-210: sealed bearings 250-449: open bearing, both sides fitted with outer and inner covers. |
| Temp. rise for bearing housing | 60℃ |
| Bearing protection | Labyrinth seal structure |
| Bearing type | Cylindrical bearings for 150-200HP 6 pole motors; Ball bearings for other motors. |
| Centered core | F1-F2 changeable at site |
| Drain plug | No drain plug |
| Efficiency | NEMA Premium Efficiency |
| End cover | End cover material : cast iron HT250 |
| Fan | Plastic or cast aluminum |
| Fan cover | Standard material: steel plate, Cast iron for severe environment Fan cover shape: coned |
| Fastener | Grade 8.8 (equivalent to SAE grade 5 ) |
| Foot flatness | Normal flatness: 0.25mm |
| Frame material | Cast iron |
| Frame size | 143-449 |
| Frequency | 60Hz 460V; 50Hz 380V |
| Lubricating grease | Mobil Polyrex EM-2 |
| Earthing | All motors have earthing screw inside terminal box. 250-449: earthing screw at frame feet. |
| Industrial standard | Primer: red iron primer; no Intermediate; Finish: polyurethane coating |
| Insulation class | Insulation class F |
| Insulation system | CNE155 The insulation system can meet the requirement of NEMA MG1-31 frequency conversion duty. |
| Inverter duty | CT:5:1; VT:10:1 |
| L10 Bearing service life | 130000 hours for direct drive; 26280 hours for belt drive; L10a 50000 |
| Lifting solution | 1 off lifting lug with inch thread per motor |
| Mounting solution | F1-F2 changeable to each other. |
| Installation hole | 4 holes in each foot Note: Only 2 holes are for installation. We set 4 holes in case of double frame sizes installation and conversion from F1 to F2. |
| NEMA Design | B |
| Lubrication | 250-449:re-lubricated structure, One lubricating nipple on end cover at DE , the other on oil pipe at NDE |
| Rotor | Cast Aluminum |
| Service factor | 1.15 1.0 when operated on a VFD. |
| Temperature control | Thermostat Harper 7/2/15, please confirm normally closed type, indicate in this spec as well. |
| Test | IEEE 112 B or CSA C390 |
| Service duty | S1 |
| Nameplate | See clause 4 |
| Packing | Wooden (details to be discussed). Suitable for fork from 2 directions for frame 447/9. |
| Warranty | Three years. |

- Name Plate Information (Typical)

| CAT.NO. |  | NEXP |  |  | FRAME | 449T | PHASE | 3 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DE BRG |  | 6318-C3 | ODE BRG | 6314-C3 | SER. | 15F4Y02AW000-01 |  |  |  |
| MAX.AMB. |  | 55℃ | INS.CLASS | F | RATING | CONT | WEIGHT | 1152KG |  |
| 60Hz | HP | 250 | RPM | 1790 | HP | 200 | RPM | 1488 | 50Hz |
|  | VOLTS | 460 |  |  | VOLTS | 380 | 415 |  |  |
|  | F.L.AMPS | 284 |  |  | F.L.AMPS | 275 | 225 |  |  |
|  | CONN. | △ |  | CODE G | CONN. | △ | △ |  |  |
|  | S.F | 1.15 |  | DESIGN B | S.F | 1.15 | DESIGN B | CODE J |  |
|  | NEMA NOM.EFF. |  | 96.20% | P.F. 0.855 | NEMA NOM.EFF. | 96.0% |  | P.F. 0.85 |  |
|  | NEMA MIN.EFF. 95.40% |  |  |  | NEMA MIN.EFF. 95.2% |  |  |  |  |
|  | MAX.KVAR | 56 |  |  |  |  |  |  |  |
| INVERTER RATED PWM VFD - 10:1VT, 5:1 CT ,1.0SF |  |  |  |  |  |  |  |  |  |

Note: Greg Harper 7/2/15:

This nameplate example does not include the actual explosion proof rating i.e. Class I, Division I etc.

At EASA I discussed with Mr. Liu the need for the different temperature codes at different ambient temperatures. I also sent him a copy of the HHI nameplate for an example. I assume this is the old nameplate. Please resubmit corrected nameplate.

- Electrical performances

Table 2 Performances at 460V 60Hz

| HP | Full Load RPM | Current (A) |  | KVAR CODE | Rotor Inertia （kg.㎡） | Efficiency (%) |  |  |  | Power Factor (%) | LRT (%) | BDT (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | FLA | LRA |  |  | 1/2 load | 3/4 load | Full load |  |  |  |  |
|  |  |  |  |  |  |  |  | Nom. | Min. |  |  |  |
| 1 | 1773 | 1.35 | 15 | N | 0.0067 | 81.3 | 84.5 | 85.5 | 82.5 | 78.5 | 311 | 412 |
| 1 | 1175 | 1.65 | 15 | N | 0.0081 | 78.0 | 81.0 | 82.5 | 80.0 | 66.0 | 342 | 341 |
| 1.5 | 3511 | 1.85 | 20 | M | 0.0026 | 83.5 | 85.1 | 84.0 | 81.5 | 84.5 | 289 | 378 |
| 1.5 | 1769 | 1.95 | 20 | M | 0.0091 | 83.0 | 86.0 | 86.5 | 84.0 | 79.0 | 291 | 377 |
| 1.5 | 1183 | 2.07 | 20 | M | 0.011 | 84.5 | 87 | 87.5 | 85.5 | 71.0 | 239 | 341 |
| 2 | 3504 | 2.5 | 25 | L | 0.0035 | 85.3 | 86.0 | 85.5 | 82.5 | 86.0 | 219 | 252 |
| 2 | 1765 | 2.6 | 25 | L | 0.017 | 84.0 | 86.0 | 86.5 | 84.0 | 83.7 | 250 | 298 |
| 2 | 1183 | 2.8 | 25 | L | 0.018 | 86.0 | 88.0 | 88.5 | 86.5 | 73.0 | 249 | 324 |
| 3 | 3528 | 3.5 | 32 | K | 0.0089 | 85.5 | 87.0 | 86.5 | 84.0 | 87.0 | 187 | 307 |
| 3 | 1761 | 3.8 | 32 | K | 0.019 | 87.5 | 89.0 | 89.5 | 87.5 | 77.0 | 232 | 322 |
| 3 | 1182 | 3.95 | 32 | K | 0.035 | 87.5 | 89.0 | 89.5 | 87.5 | 71.0 | 295 | 349 |
| 5 | 3525 | 6 | 46 | J | 0.015 | 85.0 | 87.0 | 88.5 | 86.5 | 85.0 | 177 | 306 |
| 5 | 1756 | 7 | 46 | J | 0.028 | 87.0 | 89.2 | 89.5 | 87.5 | 81.0 | 187 | 265 |
| 5 | 1178 | 7.5 | 46 | J | 0.04 | 85.0 | 89.5 | 89.5 | 87.5 | 75.0 | 222 | 275 |
| 7.5 | 3539 | 8.3 | 63.5 | H | 0.033 | 85.0 | 90.0 | 89.5 | 87.5 | 86.0 | 181 | 262 |
| 7.5 | 1773 | 8.9 | 63.5 | H | 0.036 | 89.0 | 91.5 | 91.7 | 90.2 | 84.0 | 239 | 302 |
| 7.5 | 1186 | 12.5 | 63.5 | H | 0.06 | 89.0 | 91.0 | 91.0 | 89.5 | 78.0 | 206 | 289 |
| 10 | 3540 | 11.5 | 81 | H | 0.038 | 89.0 | 90.2 | 90.2 | 88.5 | 88.0 | 183 | 264 |
| 10 | 1772 | 12.2 | 81 | H | 0.073 | 90.0 | 92.0 | 91.7 | 90.2 | 82.0 | 251 | 266 |
| 10 | 1178 | 12.5 | 81 | H | 0.065 | 89.0 | 90.0 | 91.0 | 89.5 | 81.0 | 204 | 289 |
| 15 15 15 | 3538 1767 1181 | 16.5 17.5 18.1 | 116 116 145 | G G G | 0.058 0.097 0.16 | 89.0 89.0 90.0 | 90.0 90.0 92.0 | 91.0 92.4 91.7 | 89.5 91.0 90.2 | 86.0 87.0 82.0 | 221 196 210 | 268 267 248 |
| 20 20 20 | 3531 1777 1179 | 22.8 23 23.5 | 145 145 145 | G G G | 0.065 0.18 0.20 | 88.0 90.0 89.0 | 90.0 92.0 91.5 | 91.0 93.0 91.7 | 89.5 91.7 90.2 | 88.0 87.0 81.0 | 206 193 15 5 | 245 248 240 |

| HP | Full Load RPM | Current (A) |  | KVAR CODE | Rotor Inertia （kg.㎡） | Efficiency (%) |  |  |  | Power Factor (%) | LRT (%) | BDT (%) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | FLA | LRA |  |  | 1/2 load | 3/4 load | Full load |  |  |  |  |
|  |  |  |  |  |  |  |  | Nom. | Min. |  |  |  |
| 25 | 3560 | 27.5 | 182.5 | G | 0.082 | 91.5 | 91.9 | 91.7 | 90.2 | 88.0 | 170 | 261 |
| 25 | 1778 | 27.5 | 182.5 | G | 0.24 | 93.1 | 93.6 | 93.6 | 92.4 | 85.0 | 171 | 251 |
| 25 | 1187 | 29.0 | 182.5 | G | 0.28 | 92.8 | 93.2 | 93.0 | 91.7 | 83.0 | 180 | 250 |
| 30 | 3560 | 32.5 | 217.5 | G | 0.098 | 91.5 | 91.9 | 91.7 | 90.2 | 89.0 | 179 | 265 |
| 30 | 1777 | 32.5 | 217.5 | G | 0.40 | 93.1 | 93.7 | 93.6 | 92.4 | 87.0 | 172 | 251 |
| 30 | 1187 | 37.1 | 217.5 | G | 0.33 | 92.8 | 93.2 | 93.0 | 91.7 | 78.0 | 158 | 238 |
| 40 | 3566 | 44.5 | 290.0 | G | 0.15 | 91.8 | 92.4 | 92.4 | 91.0 | 88.0 | 169 | 238 |
| 40 | 1783 | 46.0 | 290.0 | G | 0.46 | 93.9 | 94.2 | 94.1 | 93.0 | 85.0 | 186 | 252 |
| 40 | 1188 | 47.5 | 290.0 | G | 0.57 | 93.9 | 94.3 | 94.1 | 93.0 | 83.0 | 219 | 264 |
| 50 | 3573 | 54.0 | 362.5 | G | 0.18 | 92.4 | 93.0 | 93.0 | 91.7 | 88.0 | 184 | 243 |
| 50 | 1783 | 55.0 | 362.5 | G | 0.77 | 94.2 | 94.6 | 94.5 | 93.6 | 85.0 | 173 | 263 |
| 50 | 1188 | 56.5 | 362.5 | G | 0.65 | 93.9 | 94.3 | 94.1 | 93.0 | 83.0 | 209 | 256 |
| 60 | 3573 | 68.0 | 435.0 | G | 0.32 | 93.1 | 93.6 | 93.6 | 92.4 | 88.0 | 159 | 267 |
| 60 | 1786 | 70.0 | 435.0 | G | 0.87 | 94.2 | 94.9 | 95.0 | 94.1 | 85.0 | 195 | 270 |
| 60 | 1192 | 69.0 | 435.0 | G | 1.1 | 94.1 | 94.5 | 94.5 | 93.6 | 83.0 | 187 | 234 |
| 75 | 3573 | 84.5 | 542.5 | G | 0.36 | 93.2 | 93.6 | 93.6 | 92.4 | 88.0 | 172 | 277 |
| 75 | 1786 | 86.5 | 542.5 | G | 1.1 | 94.5 | 95.3 | 95.4 | 94.5 | 85.0 | 211 | 275 |
| 75 | 1192 | 89.0 | 542.5 | G | 1.3 | 94.2 | 94.6 | 94.5 | 93.6 | 83.0 | 197 | 251 |
| 100 | 3579 | 110.0 | 725.0 | G | 0.55 | 93.7 | 94.1 | 94.1 | 93.0 | 89.0 | 159 | 279 |
| 100 | 1790 | 112.0 | 725.0 | G | 1.4 | 94.8 | 95.4 | 95.4 | 94.5 | 87.0 | 199 | 247 |
| 100 | 1190 | 117.0 | 725.0 | G | 2.4 | 94.7 | 95.1 | 95.0 | 94.1 | 84.0 | 152 | 241 |
| 125 | 3586 | 130.0 | 907.5 | G | 0.79 | 94.2 | 94.8 | 95.0 | 94.1 | 89.0 | 153 | 268 |
| 125 | 1789 | 133.0 | 907.5 | G | 2.4 | 94.8 | 95.4 | 95.4 | 94.5 | 85.0 | 188 | 271 |
| 125 | 1191 | 135.0 | 907.5 | G | 2.9 | 94.7 | 95.1 | 95.0 | 94.1 | 84.0 | 148 | 246 |
| 150 | 3585 | 160.0 | 1085.0 | G | 0.97 | 94.4 | 94.9 | 95.0 | 94.1 | 87.0 | 150 | 256 |
| 150 | 1789 | 162.5 | 1085.0 | G | 2.9 | 95.7 | 95.8 | 95.8 | 95.0 | 86.0 | 164 | 262 |
| 150 | 1191 | 166.0 | 1085.0 | G | 3.5 | 95.3 | 95.8 | 95.8 | 95.0 | 82.0 | 210 | 252 |
| 200 | 3584 | 213.5 | 1450.0 | G | 1.3 | 95.0 | 95.4 | 95.4 | 94.5 | 87.0 | 168 | 264 |
| 200 | 1789 | 223.0 | 1450.0 | G | 3.5 | 95.8 | 96.2 | 96.2 | 95.4 | 85.0 | 187 | 275 |
| 200 | 1191 | 227.5 | 1450.0 | G | 4.3 | 95.5 | 95.9 | 95.8 | 95.0 | 82.0 | 157 | 263 |
| 250 | 3585 | 262.0 | 1825.0 | G | 1.6 | 95.3 | 95.7 | 95.8 | 95.0 | 87.0 | 200 | 280 |
| 250 | 1788 | 268.0 | 1825.0 | G | 4.3 | 96.0 | 96.3 | 96.2 | 95.4 | 85.0 | 228 | 244 |
| 250 | 1191 | 280.0 | 1825.0 | G | --- | 95.5 | 95.9 | 95.8 | 95.0 | 82.0 | 185 | 250 |

- Mounting & Overall Dimensions

Table 3 Dimensions for Foot-Mounted Motors with Single Straight-Shaft Extension(Inch)

Harper 7/2/15- Table 3 is missing, please insert and resubmit. Need C dimension in order to check if ‘cone’ shaped fan cover is useable.

Fig 1

Table 4 Dimensions for C Face-Mounted or Footless Motors (Inch)

| Frame Size | AJ | AK | BA* | BB Min | BC | BD Max | BF Hole |  |  | U | AH | Keyway |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | Number | Tap Size | Bolt Penetration Allowance |  |  | R | ES Min | S |
| 143TC 145TC | 5.88 | 4.5 | 2.25* | 0.16 | +0.12 | 6.5 | 4 | 3/8-16 | 0.56 | 0.875 | 2.12 | 0.771 | 1.41 | 0.188 |
| 182TC 184TC | 7.25 | 8.5 | 2.75* | 0.25 | +0.12 | 9 | 4 | 1/2-13 | 0.75 | 1.125 | 2.62 | 0.986 | 1.78 | 0.25 |
| 213TC 215TC | 7.25 | 8.5 | 3.5* | 0.25 | +0.25 | 9 | 4 | 1/2-13 | 0.75 | 1.375 | 3.12 | 1.201 | 2.41 | 0.312 |
| 254TC 256TC | 7.25 | 8.5 | 4.25* | 0.25 | +0.25 | 10 | 4 | 1/2-13 | 0.75 | 1.625 | 3.75 | 1.416 | 2.91 | 0.375 |
| 284TC 286TC | 9 | 10.5 | 4.75 | 0.25 | +0.25 | 11.25 | 4 | 1/2-13 | 0.75 | 1.875 | 4.38 | 1.591 | 3.28 | 0.500 |
| 284TSC 286TSC | 9 | 10.5 | 4.75 | 0.25 | +0.25 | 11.25 | 4 | 1/2-13 | 0.75 | 1.625 | 3.00 | 1.416 | 1.91 | 0.375 |
| 324TC 326TC | 11 | 12.5 | 5.25 | 0.25 | +0.25 | 14 | 4 | 5/8-11 | 0.94 | 2.125 | 5.00 | 1.845 | 3.91 | 0.500 |
| 324TSC 326TSC | 11 | 12.5 | 5.25 | 0.25 | +0.25 | 14 | 4 | 5/8-11 | 0.94 | 1.875 | 3.50 | 1.591 | 2.03 | 0.500 |
| 364TC 365TC | 11 | 12.5 | 5.88 | 0.25 | +0.25 | 14 | 8 | 5/8-11 | 0.94 | 2.375 | 5.62 | 2.021 | 4.28 | 0.625 |
| 364TSC 365TSC | 11 | 12.5 | 5.88 | 0.25 | +0.25 | 14 | 8 | 5/8-11 | 0.94 | 1.875 | 3.50 | 1.591 | 2.03 | 0.500 |
| 404TC 405TC | 11 | 12.5 | 6.62 | 0.25 | +0.25 | 15.5 | 8 | 5/8-11 | 0.94 | 2.875 | 7.00 | 2.450 | 5.65 | 0.750 |
| 404TSC 405TSC | 11 | 12.5 | 6.62 | 0.25 | +0.25 | 15.5 | 8 | 5/8-11 | 0.94 | 2.125 | 4.00 | 1.845 | 2.78 | 0.500 |
| 444TC 445TC | 14 | 16 | 7.5 | 0.25 | +0.25 | 18 | 8 | 5/8-11 | 0.94 | 3.375 | 8.25 | 2.880 | 6.91 | 0.875 |
| 444TSC 445TSC | 14 | 16 | 7.5 | 0.25 | +0.25 | 18 | 8 | 5/8-11 | 0.94 | 2.375 | 4.50 | 2.021 | 3.03 | 0.625 |
| 447TC 449TC | 14 | 16 | 7.5 | 0.25 | +0.25 | 18 | 8 | 5/8-11 | 0.94 | 3.375 | 8.25 | 2.880 | 6.91 | 0.875 |
| 447TSC 449TSC | 14 | 16 | 7.5 | 0.25 | +0.25 | 18 | 8 | 5/8-11 | 0.94 | 2.375 | 4.50 | 2.021 | 3.03 | 0.625 |

* For frames 143TC-256TC, dimension BA is different from NEMA MG1 4.4.4 in order to make sure it can be switched to each other from TC flange into T flange.

Fig 2